## MAIN
1 | Check switchboard is de-energized and safe.
2 | Check conformity against data sheet and project specification
3 | Check preservation status and anti-condensation heaters are ready to be energized.
4 | Check equipment is correctly aligned, leveled, rigid and secured with correct bolting,
5 | Carry out checks in acc.with vendor's procedure & check supplier's doc.
6 | Check all panel mounted devices are installed ,undamaged and tagged in accordance with data.
7 | Check if name plate data is correct.
8 | Check bus bars and supports are clean and clear of debris, torque all bolts to specifications.
9 | Check earthing and bonding of all equipment against drawings.
10 | Check gland plates (if any) and terminations are correct and suitable for external cabling.
11 | Check all switching devices are mechanically operational and undamaged.
12 | Check all the internal wiring is correctly loomed and clearly identified
13 | check all panel front component ,indicator ,lamp,meter ,relay are securely mounted and undamaged
14 | Check all circuit breakers and starter cubicles run freely in compartments
15 | Check swithgear mechanical interlocks against interlock diagram
16 | Check all C.T's &VT's are properly installed and match drawings and protection diagram.
17 | Check protection relays against protection diagram.
18 | Check all equipment are identified against drawings (cubicles, relays etc,,,)
19 | Check interconnection wiring against drawings.
20 | Check all fuses and switchgear ratings ( breakers , contactors, etc,,,)
21 | Check vendor special tools are available.
22 | Produce marked-up drawings in accordance with installation.
23 | Produce a defects list for punch list issue.
REMARKS: |  |  | PUNCH LIST ITEMS
Drawings & doc. ref.:
N.A Not Applicable |  | P: Checked & not accepted (p:punch) |  |  | Checked & accepted
Check equipment is de-energized and safe.
Check equipment is undamaged and oil levels are correct with no leaks.
Check transformer installation and mountings against drawings.
Check transformer nameplate data is correct.
Check transformer is correctly tagged.
Check cooling fans are fitted correctly, if applicable.
Check all earthing and bonding is in accordance with project specifications.
Check all terminations are clean, undamaged and correctly aligned.
Check that cables are identified and supported correctly.
CHECK LIST
Check condition of all bushing joint and seals, and that there are no fluid leaks.
Check all transformer auxiliary equipment is correclty installed (e.g Pressure and Temperature instruments).
Check tap change mechanism is correclty fitted and locked in the mid position (where applicable).
Check all termination enclosures have correct gaskets and fixing bolts.
Produce marked-up drawings in accordance with installation.
Produce a defects list for punch list issue.
Check equipment is de-energized and safe.
Check preservation status and requirements to energize anticondensation heaters.
Check equipment is correclty aligned, level, rigid and secured with correct holding down bolts.
Check all panel mounted devices are undamaged and tagged in accordance with data.
Check nameplate data is correct.
Check bus bars and supports are clean and clear of debris, torque all bolts to specification.
Check earthing and bonding of all equipment are in accordance with project specifications.
Check gland plates and terminations are correct and suitable for external cabling.
Check all switching devices are mechanically operational and undamaged.
Check all switching devices run freely in compartments and mechanical interlocks and fouling plates are correct.
Check all shutters are identified, operational and lockable.
Check all C.T's are properly installed and match data.
Check all protection relays are fitted to project schedule and tagged correctly.
Check all internal wiring is correctly loomed and clearly identified.
Check all fuses are installed in accordance with data.
Check all vendor supplied special tools and safety equipment are available.
Produce marked-up drawing in accordance with installation.
Produce a defects list for punch list issue.
Check equipment is de-energized and safe.
Check preservation status and requirements ot energize anti-condensation heaters.
Check bus bar supports/insulators are in good conditions and clean.
Check all bolts are present and torqued up to vendor's requirements.
Check all covers and cover bolts are correctly fitted and danger labels are correctly installed.
Check earthing is correct in accordance with project specification.
Check nameplate data.
Produce marked-up drawings in accordance with installation.
Produce a defects list for punch list issue.
Check cables for any physical damage.
Check cables for any physical damage.
Check equipment is de-energized and safe.
Check nameplate data is correct.
Check preservation status and requirements to energize anti-condensation heaters.
Check motor is correclty tagged.
Check motor earthing is in accordance with project specifications.
Motor uncoupled : Check direction of rotation is correct for driven equipment and that the shaft rotates free and quietly in both directions.
Check cooling system is in accordance with vendor data and is undamaged.
Check terminal boxes and terminations (Elastimolds if applicable) are suitable cable and correct for the required motor direction of rotation.
Check neutral terminal box has correclty fitted CT's.
Check (if applicable) that the bearing pedestal insulation is undamaged and clean.
Check equipment is de-energized and safe.
Check preservation status and requirements to energize anti-condensation heaters.
Check motor is correclty tagged
Check motor earthing is in accordance with project specifications.
Motor uncoupled : check direction of rotation is correct for driven equipment and that the shaft rotates free and quietly in both directions.
Check motor terminal box flange faces are clean and greased and that all bolts are present.
Produce a defects list for punch list issue.
Check the equipment is de-energized and safe.
Check preservation status.
Check motor earthing is in accordance with project specifications.
Motor uncoupled - check free and noiseless rotation in each direction.
Check brushgear is correct and that all brushes are free in boxes.
Check that spring tension on brushes conforms to vendors specifications.
Check that motor terminal box flanges are clean and greased and that all bolts are present.
Produce a list of defects for punch list issue.
Check equipment is de-energized and safe.
Check preservation status and requirements for energizing anti-condensation heaters.
Check equipment earthing and bonding is in accordance with project specifications.
Check equipment is correctly mounted, tagged and positioned in accordance with layout drawings.
Check all covers, doors, gland plates are in order and that all bolts are fitted.
Check all MCB's and ELCB's are rated and tagged in accordance with one line diagrams. Check the mechanical operation of all MCB's, ELCB's and that incoming breaker is correct.
Check all internal wiring is correct and clearly identified.
Produce marked-up drawings in accordance with installation.
Produce a list of defects for punch list issue.
Check the equipment is de-energized and safe.
Check equipment is clearly identified and tagged in accordance with layout drawings.
Check equipment is positioned correctly and is accessible and undamaged.
Check manufacturer's nameplate data.
Check all panel-front mounted components, indicators, lamps, meters are securely mounted and undamaged.
Check all internal components are undamaged.
Check all earthing and bonding are as per the specification.
Check all gland plates are suitable for external cables.
Produce marked-up drawings in accordance with installation.
Produce a defects list for punch list issue.
Check batteries are correctly installed in accordance with manufacturer's instructions with sufficient clearance and accessibility.
Check equipment is de-energized and safe.
The following Contactor Panels have been checked as per Precommissioning Check Sheet C-PX-06 Sheet 1.
The following HV cable tests must be carried out by the precommissiong contractor and witnessed by the Commissioning Department.
The following cables have been checked as per the pre-commissioning Check List C-PX-09 Sheet 1
TEST METHOD :
Continuity tests for core and armour are achieved by using one core for return and deducting this value.
Insulation tests on all cables will be as follow :
Test voltage applied between - each core and all others cores,
- each core and earth/armour.
NB: Separate earth conductors are tested as for all others cores.
The lowest value is recorded and must be withing project specification.
Notes: Continuity checks must be proved using low voltage test equipment prior to IR Megger tests.
TEST EQUIPMENT USED:
TEST METHOD :
Continuity tests for core/screen/ armour are achieved by using one core for return and deducting this value.
Insulation tests on screened singles, pairs and triples will be tested as follows:
Test voltage applied between - each core and all others cores,
- each core and screen,
- each core and earth/armour,
- each screen and all other screens,
NB: The lowest value is recorded and must be withing project specification.
Notes:Continuity checks must be proved using low voltage test equipment prior to IR Megger tests.
TEST EQUIPMENT USED:
The following cables have been checked as per the pre-commissioning Check List C-PX-10 Sheet 1.
Produce a defects list for punch list issue.
Check that the equipment is de-energized and safe.
Record on continuation sheet (s) the characteristics of circuit and check the conformity against design.
Check that all fittings are correctly mounted, accessible and that they do not clash with pipe runs and other equipment.
Check all fittings and J.B's are undamaged and are installed in accordance with layout drawings and one line diagrams.
Check circuit earthing and bonding are in conformity with project specifications.
Check all circuit idents are complete for fittings, cables and distribution board.
Produce marked-up one line diagram in accordance with installation.
Produce a defects list for punch list issue.
The following equipment has been checked as per Pre-ommissioning Check List C-PX-18 sheet 1 .
Check that the equipment is de-energized and safe.
Record on continuation sheet(s) the characteristics of circuit and the name plate data, and check conformity against one-line diagram and project data.
Check all socket outlets are undamdaged, correctly mounted, accessible, and conform to project specifications.
Check all J.B.'s are undamaged and are installed in accordance with layout drawings and one line diagrams.
Check circuit earthing is in accordance with project specifications.
Check all circuit idents are complete for fittings, cables and distribution boards.
Produce marked-up one-line diagram in accordance with installation.
Produce a defects list for punch list issue.
The following equipment has been checked as per Pre-ommissioning Check List C-PX-19 sheet 1 .
The following tapes and associated equipment have been checked as per Pre-Commissioning Check List C-PX-22 sheet 1.
TEST METHOD:
FIRST TEST:Continuity and insulation resistance tests to earth for each conductor core are carried out after the tape is installed on pipework but before any insulation and cladding is fitted.
FINAL TEST:Same as first test but carried out after pipework has been fully insulated and clad.
TEST EQUIPMENT USED:
The following Control Stations have been checked as per Pre-Commissioning Check List C-PX-23 sheet 1
Check equipment is installed in accordance with layout drawing and is undamaged.
Check that control station and additional emergency stop button are accessible and within two meters of the controlled device.
Check button/selector switch is free and operational.
Check all bolts are fitted and all unused entries are suitably plugged.
Check all earthing and bonding are in accordance with project specifications.
Produce marked-up termination drawings in accordance with installation.
Produce a defects list for punch list issue.
Complete continuation sheet C-PX-23 (Cont) for all Control Stations checked under this Check List.
Check preservation status.
Check equipment is solidly and correctly mounted and is in accordance with layout drawing.
Check nameplate data is correct.
Check equipment is tagged in accordance with layout drawings.
Check operation of isolator and interlock is correct.
Check all earthing and bonding is in accordance with project specifications.
Produce marked-up as-built termination drawings in accordance with installation.
Produce a defects list for punch list issue.
Complete continuation sheet C-PX-24 (cont) for all Isolators checked under this Check List.
The following Isolators have been checked as per Pre-Commissioning Check List C-PX-24 sheet 1
Check all equipment is correctly installed in accordance with project drawings.
Check equipment earthing and bonding are in accordance with project specifications.
Check all cable check list and test sheets have been completed.
Produce marked-up termination drawing in accordance with installation.
Produce a list of any defects for punch list issue.
Check all earth bars are installed and labelled in accordance with project drawings.
Check all earth cables are correctly installed and tagged.
Check all connections are tight, clean and coated with an approved anti-corrosive grease.
Verify earthing networks segragation actually conforms to specification.
Produce marked-up drawings in accordance with installation.
Produce a defects list for punch list issue.
Check the capacity of cable racking match the quantity and sizes of cables.
Check insulation pads are adapted to stainless steel racking.
Check that equipment is earthed and bonded in accordance with drawings and specifications.
Produce a defects list for punch list issue.
Produce marked-up layout drawing in accordance with installation.
Check cable racking is undamaged and is installed correctly in accordance with layout drawings without clashes with pipe runs or other equipment.
Check all cable rackins are adequately supported in accordance with specifications.
Check that cables segregation is correct according to project standards and specifications.
Check that MCT's conforms to project standards and specification.
Check enclosure is correctly tagged ad per drawing.
Check nameplate data/certification is in accordance with project data.
Check that terminals are approved and that the correct numbers are fitted (refer to manufacturer's certificates).
Check all gaskets and bolts are fitted in covers and gland plates where applicable (Exe)
Produce a list of defects for punch list issue.
Produce marked-up drawings in accordance with installation.
Carry out all checks as required by Manufacturer.
Check with Mechanical Department that equipment is properly installed and aligned.
Check earthing and bonding is in accordance with project specifications.
Check preservation status.
Check Nameplate data is correct.
Check equipment is de-energized and safe.
Check earthing/bonding of all equipment are in accordance with specification
Check alignment of panel and check that unit runs smoothly in and out of cubicle, and that equipment is undamaged.
Check contractor/circuit breaker rating is in accordance with data.
Check all protection devices are in accordance with data and undamaged.
Check panel is correctly tagged in accordance with general arrangement drawings.
Produce marked-up drawings in accordance with installation.
Produce a defects list for punch list issue.
Complete continuation sheet C-PX-06 (cont.) for all panels checked under this check list.
Check cables are routed in accordance with cable layout drawings.
Check cables are adequately supported and correctly fixed to rack according to project Specification.
Check all bends are within the specified limits.
Check cable is correctly loomed and segregated in accordance with specification.
Check cable and core marking are in accordance with specification.
Check glands, shrouds and earthing are in accordance with specification.
Check HV terminations are in accordance with Vendor instructions and termination diagrams, and produce "AS BUILT" termination drawings.
Check cables are as specified in project cable schedule.
Check gland plate for single core cables is non ferrous.
TEST METHOD : Refer to Pre-commissioning procedure SP-COM-511.
NOTE : Continuity cheks must be proved using low voltage test equipment prior to IR Megger tests.
TEST EQUIPMENT USED :
Check cables are routed in accordance with cable layout drawings.
Check cables are adequately supported and correctly fixed to rack according to Project Specification.
Check all bends are within the specified limits.
Check cable is correctly loomed and segregated in accordance with specification.
Check cable and core marking are in accordance with specification.
Check glands, shrouds and earthing are in accordance with specification.
Check terminations are in accordance with termination diagram, and produce "AS BUILT" terminations drawings.
Check cables are as specified in project cable schedule.
Check gland plate for single core cables is non ferrous.
Check batteries are identified and cells tagged correctly.
Check cell type and battery make-up in accordance with data.
Check all nuts and links are fitted, tightened and greased.
Check all electrolyte levels are correct (if applicable).
Check special tools and safety equipment are available.
Check room is suitably ventilated.
Produce marked-up termination drawing in accordance with installation.
Produce a defects list for punch list issue.
Check that non-magnetic gland plates are installed when using single core cables.
Produce list of defects for punch list issue.
Produce list of defects for punch list issue.
Complete continuation sheet C-P-09 for all cables checked under this check list.
Check cables for any physical damage.
Check cables are routed in accordance with cable layout drawings.
Check cables are adequately supported and correctly fixed to rack according to Project Specification.
Check all bends are within the specified limits.
Check cables is correctly loomed and segregated in accordance with specification.
Check cable and core marking is in accordance with specification.
Check glands, shrouds and earthing is in accordance with specification.
Check terminations are in accordance with termination diagram and produce "AS BUILT" termination drawings.
Check cables are as specified on project cable schedule.
Produce a defect list for punch list issue.
Carry out HV breakdown tests and record on continuation sheet(s).
Complete Continuation Sheet C-PX-10 (cont.) for all cables checked under this check list..
Check motor is correctly tagged in accordance with layout drawings.
Check motor nameplate data is correct.
Check equipment is de-energized and safe.
Check preservation status and requirements to energize anti-condensation heaters if applicable.
Check entry and terminals are correct and suitable.
Check nameplate data is correct.
Check equipment is correctly tagged as per layout drawings.
Check all earthing and bonding are in accordance with project specifications.
Produce marked-up termination drawing in accordance with installation.
Produce a defects list for punch list issue.
Check equipment is installed in accordance with layout drawing and is undamaged.
Check earthing and bonding are in accordance with project specifications.
Check equipment is correctly tagged in accordance with layout drawing.
Check nameplate data.
Produce marked-up termination drawing in accordance with installation.
Check details of circuit against design.
Check all tapes are in accordance with project data.
Check all tapes and JB's ar undamaged and are installed according to drawings.
Check circuit earthing and bonding are correct in accordance with project specifications.
Check all circuit idents are complete on tapes, cables and distribution boards.
Produce marked-up on-line diagrams in accordance with installation.
Produce a defects list for punch list issue.
Attach corresponding trace heating isometrics.
Complete continuation sheet C-PX-22 for all tapes under this Check List.
Produce a defects list for punch list issue.
Check equipment is de-energized and safe.
Check enclosure is correctly mounted and easily accessible.
Check all flange faces are clean and greased with approved lubicants, and that all bolts are fitted and correctly tight (Exd only)
Check all unused entries are plugged with approved blanks.
Check segregation barriers are fitted where necessary.
Check enclosure is correctly earthed in accordance with project data.
Produce marked-up drawings in accordance with installation.
Produce a defects list ofr punch list issue.
Complete continuation sheet C-PX-31 (Cont) for all Junction/Marshalling boxes checked under this check list.
Check panel is correctly installed in accordance with layout drawing.
Check that panel is undamaged and that all components are in good condition.
Check panel earthing and bonding are in accordance with project specifications.
Check internal wiring is correctly loomed and clearly identified.
Carry out checks in accordance with manufacturer's check list.
Produce marked-up drawings in accordance with installation.
Produce a defects list for punch list issue.
The following junction/marshalling boxes have been checked as per the Pre-Commisioning Check List C-PX-31 Sheet 1.
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF
TOTAL FINA ELF